PORTABLE FIRE EXTINGUISHERS

With proper use a portable fire extinguisher will be able to reduce or eliminate the degree of injury, damage and cost to business in the event of a small fire.

SELECTING FIRE EXTINGUISHERS

| Class of Fire | Example | Extinguisher Type |
| --- | --- | --- |
| A | Clothing, paper, cardboard, wood | Water Foam ABE Powder |
| B | Petroleum Based Products | BE and ABE Powder Foam Carbon Dioxide |
| C | Gas Fires | BE and ABE Powder |
| E | Electrical Fires Fuse Boxes | BE and ABE Powder Carbon Dioxide |
| F | Cooking Oils and Fats | Fire Blanket BE Powder |

IDENTIFYING FIRE EXTINGUISHERS

Water Fire Extinguishers - Red with No Coloured Band

Foam Fire Extinguishers - Red with a Blue Band

Powdered Fire Extinguishers - AB/ ABE - Red with a White Band

Carbon Dioxide Extinguishers - Red with a Black Band

MOUNTING FIRE EXTIGUISHERS AND SIGNS

### Extinguisher Mounting Heights

Max - 1200 mm from floor to top of extinguisher handle 
Min - 100 mm from floor to bottom of extinguisher

### Location and Sign Mounting Heights

Min - 2000 mm above floor level

- At a point that makes them visible to a person of average height and vision.

- The extinguisher or extinguisher sign shall be clearly visible for up to 20 metres on approach.

- The size of the sign shall be determined by:

  - The location at which the sign shall be legible

  - The distance at which the sign shall be legible

- A minimum of one sign must be provided above or adjacent to an extinguisher even if indicating the location of multiple or a mixed group of extinguishers.

- The extinguisher and fire point location signs shall have a symbol, border and letters in white on a red field, complying with Australian Standard AS 2700.

- The Australian Standard AS 2444 Portable Fire Extinguishers and Fire Blankets selection and location will provide comprehensive and specific information.

MAINTAINING FIRE EXTINGUISHERS

- A key factor contributing towards many workplace fires are fuel and ignition sources, a lack of appropriate fire extinguishers, training or fire extinguishers not working when required in an emergency.

- Many fires are exacerbated when maintenance is not performed or by someone who was not competent or experienced to inspect or service fire extinguishers.

- Fire extinguishers require regular inspection and regular servicing by a competent person to carry out routine or scheduled inspections and servicing.

- If portable fire extinguishers are installed in your building you are by law required to have them inspected and serviced every 6 months by a properly qualified person.

- Each extinguisher shall be located in conspicuous, readily accessible locations and have a surrounding clearance of a minimum of 1000 mm.

- Under the WHS Regulations, A PCBU must keep records in relation to tests, maintenance and inspection of fire extinguishers in the workplace.

KEEPING FIRE EXTINGUISHER MAINTENANCE RECORDS

Creates a central record for plant that can help rule out poor maintenance as a cause of incidents

WHAT SHOULD BE RECORDED?

STEP 1: RECORD THE DETAILS

- Record any maintenance done in the record of maintenance:

- the date the fire extinguisher was serviced

- who serviced the plant

- what was done

- any hazards identified

- next scheduled maintenance

STEP 2: CHECK THE DETAILS

- Keep a copy of the record of maintenance for future reference.

STEP 3: INFORM STAFF

- Make sure employees know that a piece of plant has been serviced and if the set-up or work process has changed

Property Name: …………………………………………… 			Address: ………………………………………………………………………………

| DATE | FIRE EXTINGUISHER LOCATION | SERVICE DETAILS / RESULT | NEXT SERVICE | SIGNATURE |
| --- | --- | --- | --- | --- |